## Sheet1
Routine Test Certificate
Tested Product
Commercial Reference : | [10 empty] | Serial Number :
Test Condition
Test Date: | [10 empty] | Reference Meter: |  | Radian RD30-202
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 1 | 1 | 1 | 80 | 80 | 80 | 1 | 50 | standard EN50470-1
| 2 | Imin | 1 | 1 | 1 | 80 | 80 | 80 | 1 | 60
| 3 | Itr | 2 | 2 | 2 | 100 | 100 | 100 | 0.5L | 50 | In = value of current reference (n=phase a to c)
| 4 | Itr | 2 | 2 | 2 | 100 | 100 | 100 | 0.5L | 60
| 5 | 10Itr | 20 | 20 | 20 | 230 | 230 | 230 | 0.5L | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | 10Itr | 20 | 20 | 20 | 230 | 230 | 230 | 0.5L | 60
| 7 | Imax | 125 | 125 | 125 | 332 | 332 | 332 | 0.5L | 50 | F = frequency reference
| 8 | Imax | 125 | 125 | 125 | 332 | 332 | 332 | 0.5L | 60
PF = power factor
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 |  | Ic(A): -1.5; Vc(V): 1.5
| 2 |  | Ic(A): -1.5; Vc(V): 1.5 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 |  | Ic(A): -1.5; Vc(V): 1.5
| 4 |  | Ic(A): -1.5; Vc(V): 1.5 | (Emes = measured energy, Eref = energy reference)
5 | bar: Ic(A); Vc(V)
| 6 | [9 empty] | Limit + = Maximum error tolerated defined by | bar: Ic(A); Vc(V)
| 7 | [9 empty] | standard EN50470-3 class B; | bar: Ic(A); Vc(V)
8 | bar: Ic(A); Vc(V)
The counter is declared compliant if for each Iref:
Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin