## 5A MID
Routine Test Certificate
Tested Product
Commercial Reference : | [5 empty] | A9MEM3250 |  |  |  |  | Serial Number : |  | 12333079
Test Condition
Test Date: | [10 empty] | Reference Meter: |  | CL311V2 #20112061
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 0.05 | 0.05 | 0.05 | 100 | 100 | 100 | 1 | 50 | standard EN50470-1
| 2 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | 1 | 50
| 3 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | 0.5 | 50 | In = value of current reference (n=phase a to c)
| 4 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | -0.8 | 50
| 5 | 10Itr | 5 | 5 | 5 | 277 | 277 | 277 | 1 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | 10Itr | 5 | 5 | 5 | 277 | 277 | 277 | 0.5 | 50
| 7 | 10Itr | 5 | 5 | 5 | 277 | 277 | 277 | -0.8 | 50 | F = frequency reference
| 8 | Imax | 6 | 6 | 6 | 332 | 332 | 332 | 1 | 50
| 9 | Imax | 6 | 6 | 6 | 332 | 332 | 332 | 0.5 | 50 | PF = power factor
| 10 | Imax | 6 | 6 | 6 | 332 | 332 | 332 | -0.8 | 50
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 | 0.05 | Ic(A): 0; Vc(V): 0.7
| 2 | 0.1 | Ic(A): 0; Vc(V): 0.7 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 | 0.15 | Ic(A): 0; Vc(V): 0.7
| 4 | 0.2 | Ic(A): 0; Vc(V): 0.7 | (Emes = measured energy, Eref = energy reference)
| 5 | 0.25 | Ic(A): 0; Vc(V): 0.7
| 6 | 0.3 | Ic(A): 0; Vc(V): 0.7 | Limit + = Maximum error tolerated defined by
| 7 | 0.35 | Ic(A): 0; Vc(V): 0.7 | standard EN50470-3 class B;
| 8 | 0.4 | Ic(A): 0; Vc(V): 0.7
| 9 | 0.45 | Ic(A): 0; Vc(V): 0.7 | The counter is declared compliant if for each Iref:
| 10 | 0.5 | Ic(A): 0; Vc(V): 0.7 | Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin

## 5A NON MID
Routine Test Certificate
Tested Product
Commercial Reference : | [5 empty] | A9MEM3250 |  |  |  |  | Serial Number : |  | 12333079
Test Condition
Test Date: | [10 empty] | Reference Meter: |  | CL311V2 #20112061
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 0.05 | 0.05 | 0.05 | 100 | 100 | 100 | 0.5 | 50 | standard EN50470-1
| 2 | Imin | 0.05 | 0.05 | 0.05 | 100 | 100 | 100 | 0.5 | 60
| 3 | Itr | 0.1 | 0.1 | 0.1 | 230 | 230 | 230 | 0.5 | 50 | In = value of current reference (n=phase a to c)
| 4 | Itr | 0.1 | 0.1 | 0.1 | 230 | 230 | 230 | 0.5 | 60
| 5 | 10Itr | 1 | 1 | 1 | 277 | 277 | 277 | 0.5 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | 10Itr | 1 | 1 | 1 | 277 | 277 | 277 | 0.5 | 60
| 7 | Imax | 6 | 6 | 6 | 332 | 332 | 332 | 0.5 | 50 | F = frequency reference
| 8 | Imax | 6 | 6 | 6 | 332 | 332 | 332 | 0.5 | 60
PF = power factor
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 | -0.099 | Ic(A): -1.2; Vc(V): 1.2
| 2 | -0.151 | Ic(A): -1.2; Vc(V): 1.2 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 | -0.147 | Ic(A): -1.2; Vc(V): 1.2
| 4 | -0.322 | Ic(A): -1.2; Vc(V): 1.2 | (Emes = measured energy, Eref = energy reference)
| 5 | 0.017 | Ic(A): -0.8; Vc(V): 0.8
| 6 | -0.036 | Ic(A): -0.8; Vc(V): 0.8 | Limit + = Maximum error tolerated defined by
| 7 | 0.053 | Ic(A): -0.8; Vc(V): 0.8 | standard EN50470-3 class B;
| 8 | 0.019 | Ic(A): -0.8; Vc(V): 0.8
The counter is declared compliant if for each Iref:
Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin

## 40A MID
Routine Test Certificate
Tested Product
Commercial Reference : | [5 empty] | A9MEM2020 |  |  |  |  | Serial Number : |  | WX220133810011
Test Condition
Test Date: | [10 empty] | Reference Meter: |  | CL111 #?
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 0.25 | 0.25 | 0.25 | 230 | 230 | 230 | 1 | 50 | standard EN50470-1
| 2 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | 0.5 | 50
| 3 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | 1 | 50 | In = value of current reference (n=phase a to c)
| 4 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | -0.8 | 50
| 5 | Ib | 5 | 5 | 5 | 230 | 230 | 230 | 0.5 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | Ib | 5 | 5 | 5 | 230 | 230 | 230 | 1 | 50
| 7 | Ib | 5 | 5 | 5 | 230 | 230 | 230 | -0.8 | 50 | F = frequency reference
| 8 | Imax | 40 | 40 | 40 | 230 | 230 | 230 | 0.5 | 50
| 9 | Imax | 40 | 40 | 40 | 230 | 230 | 230 | 1 | 50 | PF = power factor
| 10 | Imax | 40 | 40 | 40 | 230 | 230 | 230 | -0.8 | 50
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 | 0.05 | Ic(A): 0; Vc(V): 2
| 2 | 0.1 | Ic(A): 0; Vc(V): 2 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 | 0.15 | Ic(A): 0; Vc(V): 2
| 4 | 0.2 | Ic(A): 0; Vc(V): 2 | (Emes = measured energy, Eref = energy reference)
| 5 | 0.25 | Ic(A): 0; Vc(V): 2
| 6 | 0.3 | Ic(A): 0; Vc(V): 2 | Limit + = Maximum error tolerated defined by
| 7 | 0.35 | Ic(A): 0; Vc(V): 2 | standard EN50470-3 class B;
| 8 | 0.4 | Ic(A): 0; Vc(V): 2
| 9 | 0.45 | Ic(A): 0; Vc(V): 2 | The counter is declared compliant if for each Iref:
| 10 | 0.5 | Ic(A): 0; Vc(V): 2 | Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin

## 40A NON MID
Routine Test Certificate
Tested Product
Commercial Reference : | [5 empty] | A9MEM2010C |  |  |  |  | Serial Number : |  | WX320122930013
Test Condition
Test Date: | [10 empty] | Reference Meter: |  | CL111#
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 0.25 | 0.25 | 0.25 | 230 | 230 | 230 | 1 | 50 | standard EN50470-1
| 2 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | 1 | 50
| 3 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | 0.5 | 50 | In = value of current reference (n=phase a to c)
| 4 | Itr | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | -0.8 | 50
| 5 | Ib | 5 | 5 | 5 | 230 | 230 | 230 | 1 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | Ib | 5 | 5 | 5 | 230 | 230 | 230 | 0.5 | 50
| 7 | Ib | 5 | 5 | 5 | 230 | 230 | 230 | -0.8 | 50 | F = frequency reference
| 8 | Imax | 40 | 40 | 40 | 230 | 230 | 230 | 1 | 50
| 9 | Imax | 40 | 40 | 40 | 230 | 230 | 230 | 0.5 | 50 | PF = power factor
| 10 | Imax | 40 | 40 | 40 | 230 | 230 | 230 | -0.8 | 50
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 | -0.099 | Ic(A): -1.3; Vc(V): 1.3
| 2 | -0.151 | Ic(A): -0.8; Vc(V): 0.8 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 | -0.147 | Ic(A): -1.3; Vc(V): 1.3
| 4 | -0.322 | Ic(A): -1.3; Vc(V): 1.3 | (Emes = measured energy, Eref = energy reference)
| 5 | 0.017 | Ic(A): -0.8; Vc(V): 0.8
| 6 | -0.036 | Ic(A): -0.8; Vc(V): 0.8 | Limit + = Maximum error tolerated defined by
| 7 | 0.053 | Ic(A): -0.8; Vc(V): 0.8 | standard EN50470-3 class B;
| 8 | 0.019 | Ic(A): -0.8; Vc(V): 0.8
| 9 | -0.03 | Ic(A): -0.8; Vc(V): 0.8 | The counter is declared compliant if for each Iref:
| 10 | 0.043 | Ic(A): -0.8; Vc(V): 0.8 | Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin

## 63A MID
Routine Test Certificate
Tested Product
Commercial Reference : | [10 empty] | Serial Number :
Test Condition
Test Date: | [10 empty] | Reference Meter:
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 0.5 | 0.5 | 0.5 | 230 | 230 | 230 | 1 | 50 | standard EN50470-1
| 2 | 10Itr | 10 | 10 | 10 | 230 | 230 | 230 | 1 | 50
| 3 | 10Itr | 10 | 10 | 10 | 230 | 230 | 230 | 0.5 | 50 | In = value of current reference (n=phase a to c)
| 4 | Imax | 63 | 63 | 63 | 230 | 230 | 230 | 1 | 50
| 5 | 10Itr | 10 | 0 | 0 | 230 | 230 | 230 | 1 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | 10Itr | 0 | 10 | 0 | 230 | 230 | 230 | 1 | 50
| 7 | [9 empty] | F = frequency reference
8
| 9 | [9 empty] | PF = power factor
10
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 |  | Ic(A): 0; Vc(V): 2
| 2 |  | Ic(A): 0; Vc(V): 2 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 |  | Ic(A): 0; Vc(V): 2
| 4 |  | Ic(A): 0; Vc(V): 2 | (Emes = measured energy, Eref = energy reference)
| 5 |  | Ic(A): 0; Vc(V): 2
| 6 |  | Ic(A): 0; Vc(V): 2 | Limit + = Maximum error tolerated defined by
| 7 | [9 empty] | standard EN50470-3 class B;
8
| 9 | [9 empty] | The counter is declared compliant if for each Iref:
| 10 | [9 empty] | Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin

## 63A NON MID
Routine Test Certificate
Tested Product
Commercial Reference : | [5 empty] | A9MEM3150 |  |  |  |  | Serial Number : |  | 12333079
Test Condition
Test Date: | [10 empty] | Reference Meter: |  | CL311V2 #20112061
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 0.5 | 0.5 | 0.5 | 80 | 80 | 80 | 1 | 50 | standard EN50470-1
| 2 | Imin | 0.5 | 0.5 | 0.5 | 80 | 80 | 80 | 1 | 60
| 3 | Itr | 1 | 1 | 1 | 100 | 100 | 100 | 0.5 | 50 | In = value of current reference (n=phase a to c)
| 4 | Itr | 1 | 1 | 1 | 100 | 100 | 100 | 0.5 | 60
| 5 | 10Itr | 10 | 10 | 10 | 230 | 230 | 230 | 0.5 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | 10Itr | 10 | 10 | 10 | 230 | 230 | 230 | 0.5 | 60
| 7 | Imax | 63 | 63 | 63 | 332 | 332 | 332 | 0.5 | 50 | F = frequency reference
| 8 | Imax | 63 | 63 | 63 | 332 | 332 | 332 | 0.5 | 60
PF = power factor
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 | -0.099 | Ic(A): -1.2; Vc(V): 1.2
| 2 | -0.151 | Ic(A): -1.2; Vc(V): 1.2 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 | -0.147 | Ic(A): -1.2; Vc(V): 1.2
| 4 | -0.322 | Ic(A): -1.2; Vc(V): 1.2 | (Emes = measured energy, Eref = energy reference)
| 5 | 0.017 | Ic(A): -0.8; Vc(V): 0.8
| 6 | -0.036 | Ic(A): -0.8; Vc(V): 0.8 | Limit + = Maximum error tolerated defined by
| 7 | 0.053 | Ic(A): -0.8; Vc(V): 0.8 | standard EN50470-3 class B;
| 8 | 0.019 | Ic(A): -0.8; Vc(V): 0.8
The counter is declared compliant if for each Iref:
Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin

## 125A MID
Routine Test Certificate
Tested Product
Commercial Reference : | [10 empty] | Serial Number :
Test Condition
Test Date: | [10 empty] | Reference Meter:
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 1 | 1 | 1 | 230 | 230 | 230 | 1 | 50 | standard EN50470-1
| 2 | 10Itr | 20 | 20 | 20 | 230 | 230 | 230 | 1 | 50
| 3 | 10Itr | 20 | 20 | 20 | 230 | 230 | 230 | 0.5 | 50 | In = value of current reference (n=phase a to c)
| 4 | Imax | 125 | 125 | 125 | 230 | 230 | 230 | 1 | 50
| 5 | 10Itr | 20 | 0 | 0 | 230 | 230 | 230 | 1 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | 10Itr | 0 | 20 | 0 | 230 | 230 | 230 | 1 | 50
| 7 | [9 empty] | F = frequency reference
8
| 9 | [9 empty] | PF = power factor
10
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 |  | Ic(A): 0; Vc(V): 2
| 2 |  | Ic(A): 0; Vc(V): 2 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 |  | Ic(A): 0; Vc(V): 2
| 4 |  | Ic(A): 0; Vc(V): 2 | (Emes = measured energy, Eref = energy reference)
| 5 |  | Ic(A): 0; Vc(V): 2
| 6 |  | Ic(A): 0; Vc(V): 2 | Limit + = Maximum error tolerated defined by
| 7 | [9 empty] | standard EN50470-3 class B;
8
| 9 | [9 empty] | The counter is declared compliant if for each Iref:
| 10 | [9 empty] | Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin

## 125A NON MID
Routine Test Certificate
Tested Product
Commercial Reference : | [10 empty] | Serial Number :
Test Condition
Test Date: | [10 empty] | Reference Meter:
Temperature: |  |  |  | 23℃ ± 2 ℃ | [6 empty] | Humidity: | 50% ± 10%
Injected values :
| Item |  | Ia(A) | Ib(A) | Ic(A) | Va(V) | Vb(V) | Vc(V) | PF | F(Hz) | Iref = current reference, designation according to
| 1 | Imin | 1 | 1 | 1 | 80 | 80 | 80 | 1 | 50 | standard EN50470-1
| 2 | Imin | 1 | 1 | 1 | 80 | 80 | 80 | 1 | 60
| 3 | Itr | 2 | 2 | 2 | 100 | 100 | 100 | 0.5 | 50 | In = value of current reference (n=phase a to c)
| 4 | Itr | 2 | 2 | 2 | 100 | 100 | 100 | 0.5 | 60
| 5 | 10Itr | 20 | 20 | 20 | 230 | 230 | 230 | 0.5 | 50 | Vn = value of voltage reference (n=phase a to c)
| 6 | 10Itr | 20 | 20 | 20 | 230 | 230 | 230 | 0.5 | 60
| 7 | Imax | 125 | 125 | 125 | 332 | 332 | 332 | 0.5 | 50 | F = frequency reference
| 8 | Imax | 125 | 125 | 125 | 332 | 332 | 332 | 0.5 | 60
PF = power factor
Measured Results
| Item | MPE(%) | Ic(A): Limit -; Vc(V): Limit + | MPE(%) = measured error, defined by the formula :
| 1 |  | Ic(A): -1.5; Vc(V): 1.5
| 2 |  | Ic(A): -1.5; Vc(V): 1.5 | MPE(%) = [(Emes – Eref)/Eref]*100%
| 3 |  | Ic(A): -1.5; Vc(V): 1.5
| 4 |  | Ic(A): -1.5; Vc(V): 1.5 | (Emes = measured energy, Eref = energy reference)
5 | bar: Ic(A); Vc(V)
| 6 | [9 empty] | Limit + = Maximum error tolerated defined by | bar: Ic(A); Vc(V)
| 7 | [9 empty] | standard EN50470-3 class B; | bar: Ic(A); Vc(V)
8 | bar: Ic(A); Vc(V)
The counter is declared compliant if for each Iref:
Limit- <=MPE <= Limit+
Conformity Approval
This calibration certificate guarantees that the results
comply with the international unit system(IS) | [10 empty] | compulsory approval to validate the certificate
Zhou Lin